## Sheet1
5P Low temperature full DC frequency conversion parameter setting 220V (low temperature) |  |  | Variable | index | Modbus Address | Size | type of data | Numerical range | Remarks
User parameter setting (User mask) | Operating mode |  | CoolHeat_Mode | 0 | 40001 | 1 | int | 0~4 | 0: Koelmodus; 1: Verwarmingsmodus; 2: Warmwatermodus; 3: Warm water + koeling; 4: Warm water + verwarming;
| Heating set point |  | HeatSetP | 1 | 40002 | 1 | REAL | 10.0~CoolHeatMng.heat_set_max（CoolHeatMng.heat_set_max范围-99~100）
| Refrigeration set point |  | CoolSetP | 2 | 40003 | 1 | REAL | CoolHeatMng.cool_set_min~40.0（CoolHeatMng.cool_set_min范围-99-100.0）
| Hot water set point |  | W_TankSetP | 3 | 40004 | 1 | REAL | 10-CoolHeatMng.heat_set_max（CoolHeatMng.heat_set_max范围-99.0~100）
| Hot water hysteresis |  | hotwater_start_diff | 4 | 40005 | 1 | REAL | 1.0~15.0
| Hot water constant temperature shutdown |  | hotwater_stop_diff | 5 | 40006 | 1 | REAL | 0.0~5.0
| Cooling and heating hysteresis |  | Temp_Diff | 6 | 40007 | 1 | REAL | 1.0~15.0
| Cooling and heating constant temperature shutdown |  | Stop_TemP_Diff | 7 | 40008 | 1 | REAL | 0.0~5.0
| deviation |  | Kp | 8 | 40009 | 1 | REAL | 1.0~999.0
| Integration time |  | Ti | 9 | 40010 | 1 | UINT | 0-9999
| Differential time |  | Td | 10 | 40011 | 1 | UINT | 0-9999
| Main engine water pump |  | PmpMode | 11 | 40012 | 1 | int | 0~1 | 0: always open; 1: according to demand;
| Fan mode |  | FanMode_Sel | 12 | 40013 | 1 | int | 0~3 | 0: day mode; 1: night mode; 2: low wind mode; 3T: pressure mode;
| Electric heating control |  | En_AuxHeat | 0 | 00001 | 1 | bool
| Crankshaft/chassis electric heating control |  | En_Customer_16 | 1 | 00002 | 1 | bool
| Electric heating on delay |  | DT_AuxComp | 13 | 40014 | 1 | UINT | 0-999
| Electric heating start temperature |  | AuxHeatSetP_Exterior | 14 | 40015 | 1 | real | -30.0~20.0
| Main water pump control | Speed ​​adjustment of the temperature difference between inlet and outlet water | PmpDeltaTempSetP | 15 | 40016 | 1 | real | 2.0~15.0
| Power-down self-start |  | OnOffUnitMng.UnitTypAfterPwrOff | 2 | 00003 | 1 | bool
1
| date | year | GeneralMng.YearIn | 182 | 40183 | 1 | UINT | 0~99
| date | month | GeneralMng.MonthIn | 183 | 40184 | 1 | UINT | 0~12
| date | day | GeneralMng.DayIn | 184 | 40185 | 1 | UINT | 0~31
| time | Time | GeneralMng.HourIn | 185 | 40186 | 1 | UINT | 0~23
| time | Minute | GeneralMng.MinuteIn | 186 | 40187 | 1 | UINT | 0~59
| week |  | GeneralMng.DayOfWeek | 187 | 40188 | 1 | UINT | 1~7
| Enable time zone switch |  | En_SchedOnOff | 38 | 00039 | 1 | bool
| Enable timing change of set point |  | En_Sch_Setp | 39 | 00040 | 1 | bool
| Enable time synchronization |  | En_Date | 43 | 00044 | 1 | bool
1
1
| Unit status | Power on/off (On/Off) | UnitOn | 0 | 10001 | 1 | BOOL
B1 | Return water temperature | 0 | CW_InTemp | 188 | 40189 | 1 | REAL
B2 | Outlet temperature | 0 | CW_OutTemp | 189 | 40190 | 1 | REAL
B3 | Ambient temperature | 0 | AmbTemp | 190 | 40191 | 1 | REAL
B4 | Exhaust gas temperature | 0 | DscgTemp | 191 | 40192 | 1 | REAL
B5 | Suction temperature | 0 | SuctTemp | 192 | 40193 | 1 | REAL
B6 | High pressure | 0 | DscgP | 193 | 40194 | 1 | REAL
B7 | Low pressure | 0 | SuctP | 194 | 40195 | 1 | REAL
B8 | Hot water temperature | 0 | CW_TankTemp | 195 | 40196 | 1 | REAL
B9 | Coil temperature | 0 | CondsrCoilTemp | 196 | 40197 | 1 | REAL
ID1 | Flow switch | On/Off | InputsCheck.FlwSw_Din | 1 | 10002 | 1 | BOOL
ID2 | Emergency switch | On/Off | InputsCheck.RemoteOnOff_Din | 2 | 10003 | 1 | BOOL
ID3 | End signal switch | On/Off | InputsCheck.Terminal_Switch_Din | 3 | 10004 | 1 | BOOL
ID5 | Phase sequence protection | On/Off | InputsCheck.ProtSeqPh_Din | 4 | 10005 | 1 | BOOL
D01 | 高风 |  | Outputs.DoutVal_1 | 5 | 10006 | 1 | BOOL
D02 | Low wind |  | Outputs.DoutVal_2 | 6 | 10007 | 1 | BOOL
D03 | Four-way valve |  | Outputs.DoutVal_3 | 7 | 10008 | 1 | BOOL
D04 | Main engine water pump |  | Outputs.DoutVal_4 | 8 | 10009 | 1 | BOOL
D05 | Three-way valve |  | Outputs.DoutVal_5 | 9 | 10010 | 1 | BOOL
D06 | Electric crankshaft heating |  | Outputs.DoutVal_6 | 10 | 10011 | 1 | BOOL
D07 | Chassis electric heating |  | Outputs.DoutVal_7 | 11 | 10012 | 1 | BOOL
D09 | Electric heating |  | Outputs.DoutVal_8 | 12 | 10013 | 1 | BOOL
Y1 | Fan output |  | CondenserFan.y1_out | 197 | 40198 | 1 | REAL
Y3 | Pump output |  | Pump_Aout | 198 | 40199 | 1 | REAL
| Speed ​​control fan 1 output |  | CondenserFan.fan1_RPM_OUT_2 | 199 | 40200 | 1 | INT
| Speed ​​control fan 1 feedback |  | CondenserFan.fan2_RPM_in_2 | 200 | 40201 | 1 | INT
| Speed ​​control fan 2 output |  | CondenserFan.fan2_RPM_OUT_2 | 201 | 40202 | 1 | INT
| Speed ​​control fan 2 feedback |  | CondenserFan.fan1_RPM_in_2 | 202 | 40203 | 1 | INT
| Required cap |  | BLDC_Mng.Info_BLDC1.Info_CompRequest | 203 | 40204 | 1 | REAL
| Actual cap |  | BLDC_Mng.Info_BLDC1.Info_ReqSpeedToPWRP | 204 | 40205 | 1 | REAL
| Actual speed |  | BLDC_Mng.Info_PWRP1.Info_RotorSpeed_rps | 205 | 40206 | 1 | REAL
| Evaporation temperature |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH_EvapTemp.Val | 206 | 40207 | 1 | REAL
| Electronic expansion valve opening |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.EEV_PosSteps.Val | 207 | 40208 | 1 | INT
| Exhaust superheat |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.DscgSH.Val | 208 | 40209 | 1 | REAL
| Status | Drive status: | BLDC_Mng.Info_BLDC1.Info_HTZone | 209 | 40210 | 1 | INT |  | 0:ok 1:Controlled 2:limited
| Protection |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.ProtStatus.Val | 210 | 40211 | 1 | INT |  | 0 "None 1: None 2: LowSH 3: lop 4: Mop 5: HiTcond
| Suction SH |  | EVD_Emb_1.Params_EVDEMB_1.EVD.Variables.SH.Val | 211 | 40212 | 1 | REAL
| Unit current operating mode |  | uniton_mode | 215 | 40216 | 1 | INT |  | 0: Cooling 1: Heating 2: Hot water
| Unit switch |  | OnOffUnitMng.KeybOnOff | 40 | 00041 | 1 | bool |  | 0: Off 1: On
| Current Temperature |  | Temp_Target | 216 | 40217 | 1 | real
| Unit status |  | UnitStatus | 217 | 40218 | 1 | int | 0-10 | 0: Unit preparation; 1: Unit startup; 2: Alarm shutdown; 3: Network shutdown; 4: Monitor shutdown; 5: Emergency shutdown; 6: Button shutdown; 7: Manual mode; 8: Unit antifreeze; 9: Network switch; 10: Switch off;
| Water pump switch status |  | Pmp_On | 178 | 10179 | 1 | BOOL
| Compressor switch status |  | Comp_On | 179 | 10180 | 1 | BOOL
| Fan switch status |  | FanOn | 180 | 10181 | 1 | BOOL
| alarm reset |  | AlrmResByBms | 41 | 00042 | 1 | BOOL
Clock management | Start on Monday: Hour |  | TimezoneMng.On_Mon_Hour | 218 | 40219 | 1 | INT | 0-23
| Start on Monday: minutes |  | TimezoneMng.On_Mon_Min | 219 | 40220 | 1 | INT | 0-59
| Turn on Tuesday: Hour |  | TimezoneMng.On_Tue_Hour | 220 | 40221 | 1 | INT | 0-23
| Start on Tuesday: minutes |  | TimezoneMng.On_Tue_Min | 221 | 40222 | 1 | INT | 0-59
| Start on Wednesday: Hour |  | TimezoneMng.On_Wed_Hour | 222 | 40223 | 1 | INT | 0-23
| Start on Wednesday: minutes |  | TimezoneMng.On_Wed_Min | 223 | 40224 | 1 | INT | 0-59
| Start on Thursday: hour |  | TimezoneMng.On_Thu_Hour | 224 | 40225 | 1 | INT | 0-23
| Start on Thursday: minutes |  | TimezoneMng.On_Thu_Min | 225 | 40226 | 1 | INT | 0-59
| Start on Friday: Hour |  | TimezoneMng.On_Fri_Hour | 226 | 40227 | 1 | INT | 0-23
| Start on Friday: minutes |  | TimezoneMng.On_Fri_Min | 227 | 40228 | 1 | INT | 0-59
| Start on Saturday: hour |  | TimezoneMng.On_Sat_Hour | 228 | 40229 | 1 | INT | 0-23
| Start on Saturday: minutes |  | TimezoneMng.On_Sat_Min | 229 | 40230 | 1 | INT | 0-59
| Turn on Sunday: hours |  | TimezoneMng.On_Sun_Hour | 230 | 40231 | 1 | INT | 0-23
| Start on Sunday: minutes |  | TimezoneMng.On_Sun_Min | 231 | 40232 | 1 | INT | 0-59
| Shutdown on Monday: Hour |  | TimezoneMng.Off_Mon_Hour | 232 | 40233 | 1 | INT | 0-23
| Shutdown on Monday: minutes |  | TimezoneMng.Off_Mon_Min | 233 | 40234 | 1 | INT | 0-59
| Shutdown on Tuesday: Hour |  | TimezOffeMng.Off_Tue_Hour | 234 | 40235 | 1 | INT | 0-23
| Shutdown on Tuesday: minutes |  | TimezOffeMng.Off_Tue_Min | 235 | 40236 | 1 | INT | 0-59
| Shutdown on Wednesday: Hour |  | TimezOffeMng.Off_Wed_Hour | 236 | 40237 | 1 | INT | 0-23
| Shutdown on Wednesday: minutes |  | TimezOffeMng.Off_Wed_Min | 237 | 40238 | 1 | INT | 0-59
| Shutdown on Thursday: Hour |  | TimezOffeMng.Off_Thu_Hour | 238 | 40239 | 1 | INT | 0-23
| Shutdown on Thursday: minutes |  | TimezOffeMng.Off_Thu_Min | 239 | 40240 | 1 | INT | 0-59
| Shutdown on Friday: Hour |  | TimezOffeMng.Off_Fri_Hour | 240 | 40241 | 1 | INT | 0-23
| Shutdown on Friday: minutes |  | TimezOffeMng.Off_Fri_Min | 241 | 40242 | 1 | INT | 0-59
| Shutdown on Saturday: Hour |  | TimezOffeMng.Off_Sat_Hour | 242 | 40243 | 1 | INT | 0-23
| Shutdown on Saturday: minutes |  | TimezOffeMng.Off_Sat_Min | 243 | 40244 | 1 | INT | 0-59
| Shutdown on Sunday: Hour |  | TimezOffeMng.Off_Sun_Hour | 244 | 40245 | 1 | INT | 0-23
| Shutdown on Sunday: minutes |  | TimezOffeMng.Off_Sun_Min | 245 | 40246 | 1 | INT | 0-59
Time zone 1 management | Time |  | TimezoneMng.TempHr1 | 246 | 40247 | 1 | INT | 0-23
| Minute |  | TimezoneMng.TempMin1 | 247 | 40248 | 1 | INT | 0-59
| Refrigeration |  | TimezoneMng.S_Set_Temp1 | 248 | 40249 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp1 | 249 | 40250 | 1 | REAL | -99.0~99.0
Time zone 2 management | Time |  | TimezoneMng.TempHr2 | 250 | 40251 | 1 | INT | 0-95
| Minute |  | TimezoneMng.TempMin2 | 251 | 40252 | 1 | INT | 0-131
| Refrigeration |  | TimezoneMng.S_Set_Temp2 | 252 | 40253 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp2 | 253 | 40254 | 1 | REAL | -99.0~99.0
Time zone 3 management | Time |  | TimezoneMng.TempHr3 | 254 | 40255 | 1 | INT | 0-167
| Minute |  | TimezoneMng.TempMin3 | 255 | 40256 | 1 | INT | 0-203
| Refrigeration |  | TimezoneMng.S_Set_Temp3 | 256 | 40257 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp3 | 257 | 40258 | 1 | REAL | -99.0~99.0
Time zone 4 management | Time |  | TimezoneMng.TempHr4 | 258 | 40259 | 1 | INT | 0-239
| Minute |  | TimezoneMng.TempMin4 | 259 | 40260 | 1 | INT | 0-275
| Refrigeration |  | TimezoneMng.S_Set_Temp4 | 260 | 40261 | 1 | REAL | -99.0~99.0
| Heating |  | TimezoneMng.W_Set_Temp4 | 261 | 40262 | 1 | REAL | -99.0~99.0
| Alarm number |  | English description | index | modbus address | size | type of data |  | Chinese description
| AL000 |  | Too many mem writings | 13 | 10014 | 1 | BOOL |  | Storage type variables are frequently written frequently
| AL001 |  | Retain mem write error | 14 | 10015 | 1 | BOOL |  | Frequent alarms for writing errors in storage variables
| AL002 |  | Inlet probe error | 15 | 10016 | 1 | BOOL |  | The inlet water temperature probe is faulty or offline
| AL003 |  | Outlet probe error | 16 | 10017 | 1 | BOOL |  | The outlet water temperature probe is faulty or offline
| AL004 |  | Ambient probe error | 17 | 10018 | 1 | BOOL |  | The ambient temperature probe is faulty or offline
| AL005 |  | Condenser coil temp | 18 | 10019 | 1 | BOOL |  | The condensing coil temperature probe is faulty or offline
| AL006 |  | Water flow switch | 19 | 10020 | 1 | BOOL |  | Water flow switch alarm
| AL007 |  | Phase sequ.prot.alarm | 20 | 10021 | 1 | BOOL |  | Phase sequence protection switch alarm
| AL008 |  | Unit work hour warning | 21 | 10022 | 1 | BOOL |  | Unit working hours warning
| AL009 |  | Pump work hour warning | 22 | 10023 | 1 | BOOL |  | Water pump working time warning
| AL010 |  | Comp.work hour warning | 23 | 10024 | 1 | BOOL |  | Compressor working hours warning
| AL011 |  | Cond.fan work hourWarn | 24 | 10025 | 1 | BOOL |  | Working time of condensing fan
| AL012 |  | Low superheat - Vlv.A | 25 | 10026 | 1 | BOOL |  | EEV valve A low superheat alarm
| AL013 |  | Low superheat - Vlv.B | 26 | 10027 | 1 | BOOL |  | EEV valve B low superheat alarm
| AL014 |  | LOP - Vlv.A | 27 | 10028 | 1 | BOOL |  | EEV valve A LOP alarm
| AL015 |  | LOP - Vlv.B | 28 | 10029 | 1 | BOOL |  | EEV valve B LOP alarm
| AL016 |  | MOP - Vlv.A | 29 | 10030 | 1 | BOOL |  | EEV valve A MOP alarm
| AL017 |  | MOP - Vlv.B | 30 | 10031 | 1 | BOOL |  | EEV valve B MOP alarm
| AL018 |  | Motor error - Vlv.A | 31 | 10032 | 1 | BOOL |  | EEV valve A alarm
| AL019 |  | Motor error - Vlv.B | 32 | 10033 | 1 | BOOL |  | EEV valve B alarm
| AL020 |  | Low suct.temp. - Vlv.A | 33 | 10034 | 1 | BOOL |  | EEV valve A low suction temperature alarm
| AL021 |  | Low suct.temp. - Vlv.B | 34 | 10035 | 1 | BOOL |  | EEV valve B low suction temperature alarm
| AL022 |  | High condens.temp.EVD | 35 | 10036 | 1 | BOOL |  | EEV high condensing temperature alarm
| AL023 |  | Probe S1 error EVD | 36 | 10037 | 1 | BOOL |  | EEV S1 probe alarm
| AL024 |  | Probe S2 error EVD | 37 | 10038 | 1 | BOOL |  | EEV S2 probe alarm
| AL025 |  | Probe S3 error EVD | 38 | 10039 | 1 | BOOL |  | EEV S3 probe alarm
| AL026 |  | Probe S4 error EVD | 39 | 10040 | 1 | BOOL |  | EEV S4 probe alarm
| AL027 |  | Battery discharge EVD | 40 | 10041 | 1 | BOOL |  | EEV battery failure
| AL028 |  | EEPROM alarm EVD | 41 | 10042 | 1 | BOOL |  | EEV EEPROM alarm
| AL029 |  | Incomplete closing EVD | 42 | 10043 | 1 | BOOL |  | EEV did not completely turn off the alarm
| AL030 |  | Emergency closing EVD | 43 | 10044 | 1 | BOOL |  | EEV emergency shutdown alarm
| AL031 |  | FW not compatible EVD | 44 | 10045 | 1 | BOOL |  | EEV FW version does not match
| AL032 |  | Config. error EVD | 45 | 10046 | 1 | BOOL |  | EEV configuration error
| AL033 |  | EVD Driver offline | 46 | 10047 | 1 | BOOL |  | EEV offline alarm
| AL034 |  | BLDC-alarm:High startup DeltaP | 47 | 10048 | 1 | BOOL |  | BLDC-Starting pressure difference is too high
| AL035 |  | BLDC-alarm:Compressor shut off | 48 | 10049 | 1 | BOOL |  | BLDC-compressor off
| AL036 |  | BLDC-alarm:Out of Envelope | 49 | 10050 | 1 | BOOL |  | BLDC-Out of operating range
| AL037 |  | BLDC-alarm:Starting fail wait | 50 | 10051 | 1 | BOOL |  | BLDC-compressor failed to start
| AL038 |  | BLDC-alarm:Starting fail exceeded | 51 | 10052 | 1 | BOOL |  | BLDC-compressor failed to start
| AL039 |  | BLDC-alarm:Low delta pressure | 52 | 10053 | 1 | BOOL |  | BLDC- low dropout
| AL040 |  | BLDC-alarm:High discarge gas temp | 53 | 10054 | 1 | BOOL |  | BLDC-High exhaust temperature
| AL041 |  | Envelope-alarm:High compressor ratio | 54 | 10055 | 1 | BOOL |  | Envelope-high pressure ratio
| AL042 |  | Envelope-alarm:High discharge press. | 55 | 10056 | 1 | BOOL |  | Envelope-High exhaust pressure
| AL043 |  | Envelope-alarm:High current | 56 | 10057 | 1 | BOOL |  | Envelope-high current
| AL044 |  | Envelope-alarm:High suction pressure | 57 | 10058 | 1 | BOOL |  | Envelope-High suction pressure
| AL045 |  | Envelope-alarm:Low compressor ratio | 58 | 10059 | 1 | BOOL |  | Envelope-low pressure ratio
| AL046 |  | Envelope-alarm:Low pressure diff. | 59 | 10060 | 1 | BOOL |  | Envelope-low pressure drop
| AL047 |  | Envelope-alarm:Low discharge pressure | 60 | 10061 | 1 | BOOL |  | Envelope-low exhaust pressure
| AL048 |  | Envelope-alarm:Low suction pressure | 61 | 10062 | 1 | BOOL |  | Envelope-low suction pressure
| AL049 |  | Envelope-alarm:High discharge temp. | 62 | 10063 | 1 | BOOL |  | Envelope-High exhaust temperature
| AL050 |  | Power+ alarm:01-Overcurrent | 63 | 10064 | 1 | BOOL |  | Power+01-Overcurrent
| AL051 |  | Power+ alarm:02-Motor overload | 64 | 10065 | 1 | BOOL |  | Power+02-Motor overload
| AL052 |  | Power+ alarm:03-DCbus overvoltage | 65 | 10066 | 1 | BOOL |  | Power+03-DCbus overvoltage
| AL053 |  | Power+ alarm:04-DCbus undervoltage | 66 | 10067 | 1 | BOOL |  | Power+04-DCbus undervoltage
| AL054 |  | Power+ alarm:05-Drive overtemp. | 67 | 10068 | 1 | BOOL |  | Power+05-Inverter overheating
| AL055 |  | Power+ alarm:06-Drive undertemp. | 68 | 10069 | 1 | BOOL |  | Power+06-Inverter under temperature
| AL056 |  | Power+ alarm:07-Overcurrent HW | 69 | 10070 | 1 | BOOL |  | Power+07-Overcurrent HW
| AL057 |  | Power+ alarm:08-Motor overtemp. | 70 | 10071 | 1 | BOOL |  | Power+08-Motor overheated
| AL058 |  | Power+ alarm:09-IGBT module error | 71 | 10072 | 1 | BOOL |  | Power+09-IGBT module failure
| AL059 |  | Power+ alarm:10-CPU error | 72 | 10073 | 1 | BOOL |  | Power+10-CPU failure
| AL060 |  | Power+ alarm:11-Parameter default | 73 | 10074 | 1 | BOOL |  | Power+11- parameters are missing
| AL061 |  | Power+ alarm:12-DCbus ripple | 74 | 10075 | 1 | BOOL |  | Power+12-Bus voltage fluctuation
| AL062 |  | Power+ alarm:13-Data comm. Fault | 75 | 10076 | 1 | BOOL |  | Power+13-Data communication failure
| AL063 |  | Power+ alarm:14-Thermistor fault | 76 | 10077 | 1 | BOOL |  | Power+14-Thermistor failure
| AL064 |  | Power+ alarm:15-Autotuning fault | 77 | 10078 | 1 | BOOL |  | Power+15-Automatic adjustment failure
| AL065 |  | Power+ alarm:16-Drive disabled | 78 | 10079 | 1 | BOOL |  | Power+16-Inverter disabled
| AL066 |  | Power+ alarm:17-Motor phase fault | 79 | 10080 | 1 | BOOL |  | Power+17-motor phase sequence failure
| AL067 |  | Power+ alarm:18-Internal fan fault | 80 | 10081 | 1 | BOOL |  | Power+18-fan failure
| AL068 |  | Power+ alarm:19-Speed fault | 81 | 10082 | 1 | BOOL |  | Power+19-speed failure
| AL069 |  | Power+ alarm:20-PFC module error | 82 | 10083 | 1 | BOOL |  | Power+20-PFC module failure
| AL070 |  | Power+ alarm:21-PFC overvoltage | 83 | 10084 | 1 | BOOL |  | Power+21-PFC over voltage
| AL071 |  | Power+ alarm:22-PFC undervoltage | 84 | 10085 | 1 | BOOL |  | Power+22-PFC undervoltage
| AL072 |  | Power+ alarm:23-STO DetectionError | 85 | 10086 | 1 | BOOL |  | Power+23-STO error detection
| AL073 |  | Power+ alarm:24-STO DetectionError | 86 | 10087 | 1 | BOOL |  | Power+24-STO error detection
| AL074 |  | Power+ alarm:25-Ground fault | 87 | 10088 | 1 | BOOL |  | Power+25-ground fault
| AL075 |  | Power+ alarm:26-Internal error 1 | 88 | 10089 | 1 | BOOL |  | Power+26-CPU synchronization error 1
| AL076 |  | Power+ alarm:27-Internal error 2 | 89 | 10090 | 1 | BOOL |  | Power+27-CPU synchronization error 2
| AL077 |  | Power+ alarm:28-Drive overload | 90 | 10091 | 1 | BOOL |  | Power+28-Inverter overload
| AL078 |  | Power+ alarm:29-uC safety fault | 91 | 10092 | 1 | BOOL |  | Power+29：uC safety fault
| AL079 |  | Power+ alarm:98-Unexpected restart | 92 | 10093 | 1 | BOOL |  | Power+98：Unexpected restart
| AL080 |  | Power+ alarm:99-Unexpected stop | 93 | 10094 | 1 | BOOL |  | Power+99：Unexpected stop
| AL081 |  | Power+ safety alarm:01-Current meas.fault | 94 | 10095 | 1 | BOOL |  | Power+ safety alarm:01-Current meas.fault
| AL082 |  | Power+ safety alarm:02-Current unbalanced | 95 | 10096 | 1 | BOOL |  | Power+ safety alarm:02-Current unbalanced
| AL083 |  | Power+ safety alarm:03-Over current | 96 | 10097 | 1 | BOOL |  | Power+ safety alarm:03-Over current
| AL084 |  | Power+ safety alarm:04-STO alarm | 97 | 10098 | 1 | BOOL |  | Power+ safety alarm:04-STO alarm
| AL085 |  | Power+ safety alarm:05-STO hardware alarm | 98 | 10099 | 1 | BOOL |  | Power+ safety alarm:05-STO hardware alarm
| AL086 |  | Power+ safety alarm:06-PowerSupply missing | 99 | 10100 | 1 | BOOL |  | Power+ safety alarm:06-PowerSupply missing
| AL087 |  | Power+ safety alarm:07-HW fault cmd.buffer | 100 | 10101 | 1 | BOOL |  | Power+ safety alarm:07-HW fault cmd.buffer
| AL088 |  | Power+ safety alarm:08-HW fault heater c. | 101 | 10102 | 1 | BOOL |  | Power+ safety alarm:08-HW fault heater c.
| AL089 |  | Power+ safety alarm:09-Data comm. Fault | 102 | 10103 | 1 | BOOL |  | Power+ safety alarm:09-Data comm. Fault
| AL090 |  | Power+ safety alarm:10-Compr. stall detect | 103 | 10104 | 1 | BOOL |  | Power+ safety alarm:10-Compr. stall detect
| AL091 |  | Power+ safety alarm:11-DCbus over current | 104 | 10105 | 1 | BOOL |  | Power+ safety alarm:11-DCbus over current
| AL092 |  | Power+ safety alarm:12-HWF DCbus current | 105 | 10106 | 1 | BOOL |  | Power+ safety alarm:12-HWF DCbus current
| AL093 |  | Power+ safety alarm:13-DCbus voltage | 106 | 10107 | 1 | BOOL |  | Power+ safety alarm:13-DCbus voltage
| AL094 |  | Power+ safety alarm:14-HWF DCbus voltage | 107 | 10108 | 1 | BOOL |  | Power+ safety alarm:14-HWF DCbus voltage
| AL095 |  | Power+ safety alarm:15-Input voltage | 108 | 10109 | 1 | BOOL |  | Power+ safety alarm:15-Input voltage
| AL096 |  | Power+ safety alarm:16-HWF input voltage | 109 | 10110 | 1 | BOOL |  | Power+ safety alarm:16-HWF input voltage
| AL097 |  | Power+ safety alarm:17-DCbus power alarm | 110 | 10111 | 1 | BOOL |  | Power+ safety alarm:17-DCbus power alarm
| AL098 |  | Power+ safety alarm:18-HWF power mismatch | 111 | 10112 | 1 | BOOL |  | Power+ safety alarm:18-HWF power mismatch
| AL099 |  | Power+ safety alarm:19-NTC over temp. | 112 | 10113 | 1 | BOOL |  | Power+ safety alarm:19-NTC over temp.
| AL100 |  | Power+ safety alarm:20-NTC under temp. | 113 | 10114 | 1 | BOOL |  | Power+ safety alarm:20-NTC under temp.
| AL101 |  | Power+ safety alarm:21-NTC fault | 114 | 10115 | 1 | BOOL |  | Power+ safety alarm:21-NTC fault
| AL102 |  | Power+ safety alarm:22-HWF sync fault | 115 | 10116 | 1 | BOOL |  | Power+ safety alarm:22-HWF sync fault
| AL103 |  | Power+ safety alarm:23-Invalid parameter | 116 | 10117 | 1 | BOOL |  | Power+ safety alarm:23-Invalid parameter
| AL104 |  | Power+ safety alarm:24-FW fault | 117 | 10118 | 1 | BOOL |  | Power+ safety alarm:24-FW fault
| AL105 |  | Power+ safety alarm:25-HW fault | 118 | 10119 | 1 | BOOL |  | Power+ safety alarm:25-HW fault
| AL106 |  | Power+ safety alarm:26-reseved | 119 | 10120 | 1 | BOOL |  | Power+ safety alarm:26-reseved
| AL107 |  | Power+ safety alarm:27-reseved | 120 | 10121 | 1 | BOOL |  | Power+ safety alarm:27-reseved
| AL108 |  | Power+ safety alarm:28-reseved | 121 | 10122 | 1 | BOOL |  | Power+ safety alarm:28-reseved
| AL109 |  | Power+ safety alarm:29-reseved | 122 | 10123 | 1 | BOOL |  | Power+ safety alarm:29-reseved
| AL110 |  | Power+ safety alarm:30-reseved | 123 | 10124 | 1 | BOOL |  | Power+ safety alarm:30-reseved
| AL111 |  | Power+ safety alarm:31-reseved | 124 | 10125 | 1 | BOOL |  | Power+ safety alarm:31-reseved
| AL112 |  | Power+ safety alarm:32-reseved | 125 | 10126 | 1 | BOOL |  | Power+ safety alarm:32-reseved
| AL113 |  | Power+ alarm:Power+ offline | 126 | 10127 | 1 | BOOL |  | Inverter offline alarm
| AL114 |  | EEV alarm:Low superheat | 127 | 10128 | 1 | BOOL |  | EEV low superheat alarm
| AL115 |  | EEV alarm:LOP | 128 | 10129 | 1 | BOOL |  | EEV LOP alarm
| AL116 |  | EEV alarm:MOP | 129 | 10130 | 1 | BOOL |  | EEV MOP alarm
| AL117 |  | EEV alarm:High condens.temp. | 130 | 10131 | 1 | BOOL |  | EEV high condensing temperature alarm
| AL118 |  | EEV alarm:Low suction temp. | 131 | 10132 | 1 | BOOL |  | EEV low suction temperature alarm
| AL119 |  | EEV alarm:Motor error | 132 | 10133 | 1 | BOOL |  | EEV motor failure
| AL120 |  | EEV alarm:Self Tuning | 133 | 10134 | 1 | BOOL |  | EEV self-response PID error
| AL121 |  | EEV alarm:Emergency closing | 134 | 10135 | 1 | BOOL |  | EEV emergency shutdown alarm
| AL122 |  | EEV alarm:Temperature delta | 135 | 10136 | 1 | BOOL |  | EEV temperature difference protection
| AL123 |  | EEV alarm:Pressure delta | 136 | 10137 | 1 | BOOL |  | EEV differential pressure protection
| AL124 |  | EEV alarm:Param.range error | 137 | 10138 | 1 | BOOL |  | EEV range error
| AL125 |  | EEV alarm:ServicePosit% err | 138 | 10139 | 1 | BOOL |  | EEV position signal error
| AL126 |  | EEV alarm:ValveID pin error | 139 | 10140 | 1 | BOOL |  | EEV serial number error
| AL127 |  | Low press alarm | 140 | 10141 | 1 | BOOL |  | Low pressure alarm
| AL128 |  | High press alarm | 141 | 10142 | 1 | BOOL |  | High voltage alarm
| AL129 |  | Disc.temp.probe error | 142 | 10143 | 1 | BOOL |  | Exhaust temperature probe alarm
| AL130 |  | Suct.temp.probe error | 143 | 10144 | 1 | BOOL |  | Inspiratory temperature probe alarm
| AL131 |  | Disc.press.probe error | 144 | 10145 | 1 | BOOL |  | Exhaust pressure probe alarm
| AL132 |  | Suct.press.probe error | 145 | 10146 | 1 | BOOL |  | Inspiratory pressure probe alarm
| AL133 |  | Tank temp.probe error | 146 | 10147 | 1 | BOOL |  | Water tank temperature probe alarm
| AL134 |  | EVI SuctT.probe error | 147 | 10148 | 1 | BOOL |  | EVI suction temperature probe alarm
| AL135 |  | EVI SuctP.probe error | 148 | 10149 | 1 | BOOL |  | EVI suction pressure probe alarm
| AL136 |  | Flow switch alarm | 149 | 10150 | 1 | BOOL |  | Water flow switch alarm
| AL137 |  | High temp. alarm | 150 | 10151 | 1 | BOOL |  | High water temperature alarm
| AL138 |  | Low temp. alarm | 151 | 10152 | 1 | BOOL |  | Low water temperature alarm
| AL139 |  | Temp.delta alarm | 152 | 10153 | 1 | BOOL |  | Inlet and outlet water temperature difference alarm
| AL140 |  | EVI alarm:Param.range error | 153 | 10154 | 1 | BOOL |  | EVI range error
| AL141 |  | EVI alarm:Low superheat | 154 | 10155 | 1 | BOOL |  | EVI low superheat alarm
| AL142 |  | EVI alarm:LOP | 155 | 10156 | 1 | BOOL |  | EVI LOP alarm
| AL143 |  | EVI alarm:MOP | 156 | 10157 | 1 | BOOL |  | EVI MOP alarm
| AL144 |  | EVI alarm:High condens.temp. | 157 | 10158 | 1 | BOOL |  | EVI high condensing temperature alarm
| AL145 |  | EVI alarm:Low suction temp. | 158 | 10159 | 1 | BOOL |  | EVI low suction temperature alarm
| AL146 |  | EVI alarm:Motor error | 159 | 10160 | 1 | BOOL |  | EVI motor failure
| AL147 |  | EVI alarm:Self Tuning | 160 | 10161 | 1 | BOOL |  | EVI adaptive PID error
| AL148 |  | EVI alarm:Emergency closing | 161 | 10162 | 1 | BOOL |  | EVI emergency shutdown
| AL149 |  | EVI alarm:ServicePosit% err | 162 | 10163 | 1 | BOOL |  | EVI position signal error
| AL150 |  | EVI alarm:ValveID pin error | 163 | 10164 | 1 | BOOL |  | EVI serial number error
| AL151 |  | Supply power error | 164 | 10165 | 1 | BOOL |  | Power frequency fluctuation alarm
| AL152 |  | Fan1 fault | 165 | 10166 | 1 | BOOL |  | Speed ​​control fan 1 failure
| AL153 |  | Fan2 fault | 166 | 10167 | 1 | BOOL |  | Speed ​​control fan 2 failure
| AL154 |  | Fans Offline | 167 | 10168 | 1 | BOOL |  | Speed ​​control fan communication is offline
| AL164 |  | Slave1 Offline | 168 | 10169 | 1 | BOOL |  | 1#The slave is offline
| AL165 |  | Master Offline | 169 | 10170 | 1 | BOOL |  | Host is offline
| AL166 |  | Slave2 Offline | 170 | 10171 | 1 | BOOL |  | 2#The slave is offline
| AL167 |  | Slave3 Offline | 171 | 10172 | 1 | BOOL |  | 3#Slave offline
| AL168 |  | Slave4 Offline | 172 | 10173 | 1 | BOOL |  | 4#Slave offline
| AL169 |  | Slave5 Offline | 173 | 10174 | 1 | BOOL |  | 5#Slave offline
| AL170 |  | Slave6 Offline | 174 | 10175 | 1 | BOOL |  | 6#Slave offline
| AL171 |  | Slave7 Offline | 175 | 10176 | 1 | BOOL |  | 7#Slave offline
| AL172 |  | Slave8 Offline | 176 | 10177 | 1 | BOOL |  | 8#The slave is offline
| AL173 |  | Slave9 Offline | 177 | 10178 | 1 | BOOL |  | 9#Slave offline

## Sheet2
Modbus settings
| Baudrate | 19600
| Slave address | 1
| Data | 8
| Stop bit | 2
| Parity format | N