## Sheet1
DC inverter | APP Changing point | index | modbus address |  | Data type |  | Value | remark | Remark
Main interface | Work mode select | 0 | 40001 | 1 | int | Read/write | 0~4 | 0:cooling ;1:heating ;2:hot water ;3:hot water +cooling ;4:hot water +heating ; | 0:Cooling ;1:Heating ;2:Hot water ;3:Hotwater+cool;4:Hotwater+heat;
| Heating setp. | 1 | 40002 | 1 | REAL | Read/write | 10.0~CoolHeatMng.heat_set_max（CoolHeatMng.heat_set_max范围-99~100）
| Cooling setp. | 2 | 40003 | 1 | REAL | Read/write | CoolHeatMng.cool_set_min~40.0（CoolHeatMng.cool_set_min范围-99-100.0）
| Hotwater setp. | 3 | 40004 | 1 | REAL | Read/write | 10-CoolHeatMng.heat_set_max（CoolHeatMng.heat_set_max范围-99.0~100）
| On/Off status | 0 | 10001 | 1 | BOOL | Read
| Status | 217 | 40218 | 1 | int | Read | 0-10 | 0:机组准备;1:机组开机;2:报警关机;3:网络关机;4:监控关机;5:紧急关机;6:按键关机;7:手动模式;8:机组防冻;9:联网开关;10:转换关机; | 0:Unit not Ready;1:Unit ON;2:OFF by Alarm;3:OFF by Timezone;4:OFF by SuperV;5:OFF by linkage.;6:OFF by Keyboad;7:Manual Mode;8:Anti Freeze;9:OFF by AC linkage;10:OFF by Change;
| Unit on/off | 40 | 00041 | 1 | bool | Read/write |  | 0：关 1：开 | 0：Disable 1：Enable
| Temp. | 216 | 40217 | 1 | real | Read
| Work mode select | 215 | 40216 | 1 | INT | Read/write |  | 0：制冷 1：制热 2：热水 | 0：Cooling 1：Heating 2：Hot water
| Fan mode | 12 | 40013 | 1 | int | Read/write | 0~3 | 0:白天模式;1:夜间模式;2:低风模式;3T:压力模式; | 0:Daytime;1:Night;2:Low speed;3T:Pressure;
| Pump | 178 | 10179 | 1 | BOOL | Read
| Comp. | 179 | 10180 | 1 | BOOL | Read
| Fan | 180 | 10181 | 1 | BOOL | Read
Inquiry interface | Program version 1 | 325 | 40326 | 1 | INT | Read
| Program version 2 | 326 | 40327 | 1 | INT | Read
| Program version 3 | 327 | 40328 | 1 | INT | Read
| HeatPump model 1 | 328 | 40329 | 1 | INT | Read
| HeatPump model 2 | 329 | 40330 | 1 | INT | Read
| B1: Inlet temp. | 188 | 40189 | 1 | REAL | Read
| B2: Outlet temp. | 189 | 40190 | 1 | REAL | Read
| B3:Ext temp. | 190 | 40191 | 1 | REAL | Read
| B4:Disch. gas temp. | 191 | 40192 | 1 | REAL | Read
| B5:Suct. gas temp. | 192 | 40193 | 1 | REAL | Read
| B6:Disch. press. | 193 | 40194 | 1 | REAL | Read
| B7:Suct. press. | 194 | 40195 | 1 | REAL | Read
| B8:Hotwater temp. | 195 | 40196 | 1 | REAL | Read
| B9:Coil temp. | 196 | 40197 | 1 | REAL | Read
| ID1: Flow switch | 1 | 10002 | 1 | BOOL | Read
| ID2: Linkage switch | 2 | 10003 | 1 | BOOL | Read
| ID3: A/C Linkage switch | 3 | 10004 | 1 | BOOL | Read
| ID4: Cooling linkage | 181 | 10182 | 1 | BOOL | Read
| ID5: Phase. switch | 4 | 10005 | 1 | BOOL | Read
| ID6: Heating linkage | 182 | 10183 | 1 | BOOL | Read
| D01: Fan high speed | 5 | 10006 | 1 | BOOL | Read
| D02: Fan low speed | 6 | 10007 | 1 | BOOL | Read
| D03: 4 way valve | 7 | 10008 | 1 | BOOL | Read
| D04: Pump | 8 | 10009 | 1 | BOOL | Read
| D05: Chassis heater | 9 | 10010 | 1 | BOOL | Read
| D06: Crank heater | 10 | 10011 | 1 | BOOL | Read
| D07: Three valve | 11 | 10012 | 1 | BOOL | Read
| D08: Terminal Pump | 183 | 10184 | 1 | BOOL | Read
| D09: Heater | 12 | 10013 | 1 | BOOL | Read
| Y1: Fan output | 197 | 40198 | 1 | REAL | Read
| Y3: Pump output | 198 | 40199 | 1 | REAL | Read
| DC Fan 1 Output | 199 | 40200 | 1 | INT | Read
| DC Fan 1 Feedback | 200 | 40201 | 1 | INT | Read
| DC Fan 2 Output | 201 | 40202 | 1 | INT | Read
| DC Fan 2 Feedback | 202 | 40203 | 1 | INT | Read
| EEV opening | 207 | 40208 | 1 | INT | Read
| Compr. capacity regul. Required cap. | 203 | 40204 | 1 | REAL | Read
| Actual cap. | 204 | 40205 | 1 | REAL | Read
| Acutal speed | 205 | 40206 | 1 | REAL | Read
| Status | 209 | 40210 | 1 | INT | Read |  | 0:ok 1:Controlled 2:limited | 0:ok 1:Controlled 2:limited
| Protection | 210 | 40211 | 1 | INT | Read |  | 0“无 1：无 2：LowSH 3：lop 4:Mop 5:HiTcond | 0“无 1：无 2：LowSH 3：lop 4:Mop 5:HiTcond
| Suction SH | 211 | 40212 | 1 | REAL | Read
Timing | Year | 182 | 40183 | 1 | UINT | Read/write | 0~99
| Month | 183 | 40184 | 1 | UINT | Read/write | 0~12
| Day | 184 | 40185 | 1 | UINT | Read/write | 0~31
| Hour | 185 | 40186 | 1 | UINT | Read/write | 0~23
| Minute | 186 | 40187 | 1 | UINT | Read/write | 0~59
| Week | 187 | 40188 | 1 | UINT | Read/write | 1~7
| Timezone onoff | 38 | 00039 | 1 | bool | Read/write
| Timezone setpoint | 39 | 00040 | 1 | bool | Read/write
|  | 43 | 00044 | 1 | bool | Read/write
| Mon. ON: hour | 218 | 40219 | 1 | INT | Read/write | 0-23
| Mon. ON: minute | 219 | 40220 | 1 | INT | Read/write | 0-59
| Tue. ON: hour | 220 | 40221 | 1 | INT | Read/write | 0-23
| Tue. ON: minute | 221 | 40222 | 1 | INT | Read/write | 0-59
| Wed. ON: hour | 222 | 40223 | 1 | INT | Read/write | 0-23
| Wed. ON: minute | 223 | 40224 | 1 | INT | Read/write | 0-59
| Thu. ON: hour | 224 | 40225 | 1 | INT | Read/write | 0-23
| Thu. ON: minute | 225 | 40226 | 1 | INT | Read/write | 0-59
| Fri. ON: hour | 226 | 40227 | 1 | INT | Read/write | 0-23
| Fri. ON: minute | 227 | 40228 | 1 | INT | Read/write | 0-59
| Sat. ON: hour | 228 | 40229 | 1 | INT | Read/write | 0-23
| Sat. ON: minute | 229 | 40230 | 1 | INT | Read/write | 0-59
| Sun. ON: hour | 230 | 40231 | 1 | INT | Read/write | 0-23
| Sun. ON: minute | 231 | 40232 | 1 | INT | Read/write | 0-59
| Mon. OFF: hour | 232 | 40233 | 1 | INT | Read/write | 0-23
| Mon. OFF: minute | 233 | 40234 | 1 | INT | Read/write | 0-59
| Tue. OFF: hour | 234 | 40235 | 1 | INT | Read/write | 0-23
| Tue. OFF: minute | 235 | 40236 | 1 | INT | Read/write | 0-59
| Wed. OFF: hour | 236 | 40237 | 1 | INT | Read/write | 0-23
| Wed. OFF: minute | 237 | 40238 | 1 | INT | Read/write | 0-59
| Thu. OFF: hour | 238 | 40239 | 1 | INT | Read/write | 0-23
| Thu. OFF: minute | 239 | 40240 | 1 | INT | Read/write | 0-59
| Fri. OFF: hour | 240 | 40241 | 1 | INT | Read/write | 0-23
| Fri. OFF: minute | 241 | 40242 | 1 | INT | Read/write | 0-59
| Sat. OFF: hour | 242 | 40243 | 1 | INT | Read/write | 0-23
| Sat. OFF: minute | 243 | 40244 | 1 | INT | Read/write | 0-59
| Sun. OFF: hour | 244 | 40245 | 1 | INT | Read/write | 0-23
| Sun. OFF: minute | 245 | 40246 | 1 | INT | Read/write | 0-59
| Hour | 246 | 40247 | 1 | INT | Read/write | 0-23
| Minute | 247 | 40248 | 1 | INT | Read/write | 0-59
| Cooling temp. | 248 | 40249 | 1 | REAL | Read/write | -99.0~99.0
| Heating temp. | 249 | 40250 | 1 | REAL | Read/write | -99.0~99.0
| Hour | 250 | 40251 | 1 | INT | Read/write | 0-95
| Minute | 251 | 40252 | 1 | INT | Read/write | 0-131
| Cooling temp. | 252 | 40253 | 1 | REAL | Read/write | -99.0~99.0
| Heating temp. | 253 | 40254 | 1 | REAL | Read/write | -99.0~99.0
| Hour | 254 | 40255 | 1 | INT | Read/write | 0-167
| Minute | 255 | 40256 | 1 | INT | Read/write | 0-203
| Cooling temp. | 256 | 40257 | 1 | REAL | Read/write | -99.0~99.0
| Heating temp. | 257 | 40258 | 1 | REAL | Read/write | -99.0~99.0
| Hour | 258 | 40259 | 1 | INT | Read/write | 0-239
| Minute | 259 | 40260 | 1 | INT | Read/write | 0-275
| Cooling temp. | 260 | 40261 | 1 | REAL | Read/write | -99.0~99.0
| Heating temp. | 261 | 40262 | 1 | REAL | Read/write | -99.0~99.0
Project paramters | Hot watet setp. Temp. diff. | 4 | 40005 | 1 | REAL | Read/write | 1.0~15.0
| Stop temp. diff. | 5 | 40006 | 1 | REAL | Read/write | 0.0~5.0
| Cool and heat mode Temp. diff. | 6 | 40007 | 1 | REAL | Read/write | 1.0~15.0
| Stop temp. diff. | 7 | 40008 | 1 | REAL | Read/write | 0.0~5.0
| Pump work | 11 | 40012 | 1 | int | Read/write | 0~1 | 0: 一直开;1:根据需求;2间歇开 | 0: Normal;1:Demand;2Interval
| Auto Start | 2 | 00003 | 1 | bool | Read/write
| Unit mode | 42 | 00043 | 1 | BOOL | Read/write | 0~1 | 0~1 | 0：Hot water on 1：Hot water off
| Cool minimum set | 72 | 40073 | 1 | real | Read/write | -99~100
| Heat maximum set | 73 | 40074 | 1 | real | Read/write | -99~100
| Address | 74 | 40075 | 2 | udint | Read/write | 1-207
| Network EN | 34 | 00035 | 1 | bool | Read/write
| Enable heater | 323 | 40324 | 1 | INT | Read/write | 0：Disable 1：Hotwater 2：Heating 3：All |  | 0：Disable 1：Hotwater 2：Heating 3：All
| Enable chassis/crack heater | 1 | 00002 | 1 | bool | Read/write
| E/H Comp. delay | 13 | 40014 | 1 | UINT | Read/write | 0-999
| Ext. temp. setp. | 14 | 40015 | 1 | real | Read/write | -30.0~20.0
| Delta temp. set | 15 | 40016 | 1 | real | Read/write | 2.0~15.0
| Pump Auto | 47 | 00048 | 1 | BOOL | Read/write | 0：Disable 1：Enable |  | 0：Disable 1：Enable
| Enable_AmbTemp_Switch | 52 | 00053 | 1 | bool | Read/write | 0：Disable 1：Enable |  | 0：Disable 1：Enable
| Amb_switch_SetP | 297 | 40298 | 1 | real | Read/write | 10.0~30.0
| Amb_switch_Offs | 298 | 40299 | 1 | real | Read/write | 0.0~20.0
| MIN_pump off Time | 299 | 40300 | 1 | int | Read/write | 1~99min
| A/C Water Temp correct | 300 | 40301 | 1 | real | Read/write | 0.0~99.0
| Outlet water Temp correct | 301 | 40302 | 1 | real | Read/write | 0.0~99.0
| Ambient Temp correct | 302 | 40303 | 1 | real | Read/write | 0.0~99.0
| Outlet gas Temp correct | 303 | 40304 | 1 | real | Read/write | 0.0~99.0
| Inlet gas Temp correct | 304 | 40305 | 1 | real | Read/write | 0.0~99.0
| High pressure sensor | 305 | 40306 | 1 | real | Read/write | 0.0~99.0
| Low pressure sensor | 306 | 40307 | 1 | real | Read/write | 0.0~99.0
| Hot water Temp correct | 307 | 40308 | 1 | real | Read/write | 0.0~99.0
| Air HE coil Temp correct | 308 | 40309 | 1 | real | Read/write | 0.0~99.0
| Network Settings | 35 | 00036 | 1 | bool | Read/write |  | 0:从机;1:主机; | 0:Slave;1:Master;
| Insert new service passwoManufact | 76 | 40077 | 1 | Uint | Read/write | 0~9999
| Manual insert BLDC parameter | 13 | 00014 | 1 | BOOL | / | 0：No 1：yes | 无此变量
| Insert BLDC default | 332 | 40333 | 1 | int | / | 0：No 1：yes
| Restore PCB default | 57 | 00058 | 1 | bool | / | 0：No 1：yes
| BLDC Mot Power W | 333 | 40334 | 1 | real | Read
| BLDC Mot Power V | 334 | 40335 | 1 | int | Read
| BLDC Mot Power A | 335 | 40336 | 1 | real | Read
| Fan NightMode Comp max Speed（rps） | 263 | 40264 | 1 | real | Read/write | 0.0~MaxSpeedRps
| Fan NightMode Fan max Speed（rps） | 264 | 40265 | 1 | real | Read/write | 0-1000.0
| 4<AmbTemp<=9 | 265 | 40266 | 1 | real | Read/write | 0.0~MaxSpeedRps
| -3< AmbTemp <=4 | 266 | 40267 | 1 | real | Read/write | 0.0~MaxSpeedRps
| -9<AmbTemp<=-3 | 267 | 40268 | 1 | real | Read/write | 0.0~MaxSpeedRps
| -15<AmbTemp<=-9 | 268 | 40269 | 1 | real | Read/write | 0.0~MaxSpeedRps
| AmbTemp<=-15 | 269 | 40270 | 1 | real | Read/write | 0.0~MaxSpeedRps
| 9<AmbTemp | 270 | 40271 | 1 | real | Read/write | 0.0~MaxSpeedRps
| 38<AmbTemp | 271 | 40272 | 1 | real | Read/write | 0.0~MaxSpeedRps
| 33<AmbTemp<=38 | 272 | 40273 | 1 | real | Read/write | 0.0~MaxSpeedRps
| 30<AmbTemp<=33 | 273 | 40274 | 1 | real | Read/write | 0.0~MaxSpeedRps
| 26<AmbTemp<=30 | 274 | 40275 | 1 | real | Read/write | 0.0~MaxSpeedRps
| AmbTemp<=26 | 275 | 40276 | 1 | real | Read/write | 0.0~MaxSpeedRps
| Cooling mode Amb. X1 | 276 | 40277 | 1 | real | Read/write | -99.9~99.9
| Cooling mode Amb. X2 | 277 | 40278 | 1 | real | Read/write | -99.9~99.9
| Cooling mode Amb. X3 | 278 | 40279 | 1 | real | Read/write | -99.9~99.9
| Cooling mode Amb. X4 | 279 | 40280 | 1 | real | Read/write | -99.9~99.9
| Heating mode Amb. X1 | 280 | 40281 | 1 | real | Read/write | -99.9~99.9
| Heating mode Amb. X2 | 281 | 40282 | 1 | real | Read/write | -99.9~99.9
| Heating mode Amb. X3 | 282 | 40283 | 1 | real | Read/write | -99.9~99.9
| Heating mode Amb. X4 | 283 | 40284 | 1 | real | Read/write | -99.9~99.9
| H.W mode Amb. X1 | 284 | 40285 | 1 | real | Read/write | -99.9~99.9
| H.W mode Amb. X2 | 285 | 40286 | 1 | real | Read/write | -99.9~99.9
| H.W mode Amb. X3 | 286 | 40287 | 1 | real | Read/write | -99.9~99.9
| H.W mode Amb. X4 | 287 | 40288 | 1 | real | Read/write | -99.9~99.9
| Cooling mode Water Y1 | 336 | 40289 | 1 | real | Read/write | -99.9~99.9
| Cooling mode Water Y2 | 288 | 40289 | 1 | real | Read/write | -99.9~99.9
| Cooling mode Water Y3 | 289 | 40290 | 1 | real | Read/write | -99.9~99.9
| Cooling mode Water Y4 | 290 | 40291 | 1 | real | Read/write | -99.9~99.9
| Heating mode Water Y1 | 291 | 40292 | 1 | real | Read/write | -99.9~99.9
| Heating mode Water Y2 | 292 | 40293 | 1 | real | Read/write | -99.9~99.9
| Heating mode Water Y3 | 293 | 40294 | 1 | real | Read/write | -99.9~99.9
| Heating mode Water Y4 | 337 | 40294 | 1 | real | Read/write | -99.9~99.9
| H.W mode Water Y1 | 294 | 40295 | 1 | real | Read/write | -99.9~99.9
| H.W mode Water Y2 | 295 | 40296 | 1 | real | Read/write | -99.9~99.9
| H.W mode Water Y3 | 296 | 40297 | 1 | real | Read/write | -99.9~99.9
| H.W mode Water Y4 | 338 | 40297 | 1 | real | Read/write | -99.9~99.9
Defrost parameter | Defrost EN | 36 | 00037 | 1 | BOOL | Read/write
| Defrost Min. speed when change | 77 | 40078 | 1 | REAL | Read/write | 30.0~90.0
| Defrost EEV opening | 78 | 40079 | 1 | INT | Read/write | 0-480
| EEV opening when defrost quit | 79 | 40080 | 1 | INT | Read/write | 0-480
| EEV opening keep time | 80 | 40081 | 1 | INT | Read/write | 0~999
| Compressor speed for defrost | 81 | 40082 | 1 | REAL | Read/write | 30.0~oil_defrost_maxspeed（oil_defrost_maxspeed 0.0~120.0）
| Pump speed for defrost | 82 | 40083 | 1 | REAL | Read/write | 0.0~100.0
| Defrost start setpoint | 83 | 40084 | 1 | REAL | Read/write | -20.0~30.0
| Defrost end setpoint | 84 | 40085 | 1 | REAL | Read/write | 0.0~30.0
| Defrost Amb. setpoint | 85 | 40086 | 1 | REAL | Read/write | -30.0~30.0
| Defrost Amb and coil T.diff. | 86 | 40087 | 1 | REAL | Read/write | 1.0~30.0
| Defrost delay | 87 | 40088 | 1 | UINT | Read/write | 0~90
| Defrost min. time | 88 | 40089 | 1 | UINT | Read/write | 1-99
| Defrost max. time | 89 | 40090 | 1 | UINT | Read/write | 1~99
| Defrost interval time | 90 | 40091 | 1 | UINT | Read/write | 0-480
| Automatic defrost every | 91 | 40092 | 1 | UINT | Read/write | 1~999
Error history | Alarm reset | 41 | 00042 | 1 | BOOL | Read/write
|  | index | modbus address |  | data type |  |  | 中文描述
| AL001 Too many mem writings | 13 | 10014 | 1 | BOOL | Read |  | 存贮类型变量频繁write频繁
| AL002 Retain mem write error | 14 | 10015 | 1 | BOOL | Read |  | 存贮变量write错误报警频繁
| AL003 Inlet probe error | 15 | 10016 | 1 | BOOL | Read |  | 进水温度探头故障或离线
| AL004 Outlet probe error | 16 | 10017 | 1 | BOOL | Read |  | 出水温度探头故障或离线
| AL005 Ambient probe error | 17 | 10018 | 1 | BOOL | Read |  | 环境温度探头故障或离线
| AL006 Condenser coil temp | 18 | 10019 | 1 | BOOL | Read |  | 冷凝盘管温度探头故障或离线
| AL007 Water flow switch | 19 | 10020 | 1 | BOOL | Read |  | 水流开关报警
| AL008 Phase sequ.prot.alarm | 20 | 10021 | 1 | BOOL | Read |  | 相序保护开关报警
| AL009 Unit work hour warning | 21 | 10022 | 1 | BOOL | Read |  | 机组工作时间警告
| AL010 Pump work hour warning | 22 | 10023 | 1 | BOOL | Read |  | 水泵工作时间警告
| AL011 Comp.work hour warning | 23 | 10024 | 1 | BOOL | Read |  | 压缩机工作时间警告
| AL012 Cond.fan work hourWarn | 24 | 10025 | 1 | BOOL | Read |  | 冷凝风机工作时间
| AL013 Low superheat - Vlv.A | 25 | 10026 | 1 | BOOL | Read |  | EEV阀A低过热度报警
| AL014 Low superheat - Vlv.B | 26 | 10027 | 1 | BOOL | Read |  | EEV阀B低过热度报警
| AL015 LOP - Vlv.A | 27 | 10028 | 1 | BOOL | Read |  | EEV阀A LOP报警
| AL016 LOP - Vlv.B | 28 | 10029 | 1 | BOOL | Read |  | EEV阀B LOP报警
| AL017 MOP - Vlv.A | 29 | 10030 | 1 | BOOL | Read |  | EEV阀A MOP报警
| AL018 MOP - Vlv.B | 30 | 10031 | 1 | BOOL | Read |  | EEV阀B MOP报警
| AL019 Motor error - Vlv.A | 31 | 10032 | 1 | BOOL | Read |  | EEV阀A 报警
| AL020 Motor error - Vlv.B | 32 | 10033 | 1 | BOOL | Read |  | EEV阀B 报警
| AL021 Low suct.temp. - Vlv.A | 33 | 10034 | 1 | BOOL | Read |  | EEV阀A低吸气温度报警
| AL022 Low suct.temp. - Vlv.B | 34 | 10035 | 1 | BOOL | Read |  | EEV阀B低吸气温度报警
| AL023 High condens.temp.EVD | 35 | 10036 | 1 | BOOL | Read |  | EEV高冷凝温度报警
| AL024 Probe S1 error EVD | 36 | 10037 | 1 | BOOL | Read |  | EEV S1 探头报警
| AL025 Probe S2 error EVD | 37 | 10038 | 1 | BOOL | Read |  | EEV S2 探头报警
| AL026 Probe S3 error EVD | 38 | 10039 | 1 | BOOL | Read |  | EEV S3 探头报警
| AL027 Probe S4 error EVD | 39 | 10040 | 1 | BOOL | Read |  | EEV S4 探头报警
| AL028 Battery discharge EVD | 40 | 10041 | 1 | BOOL | Read |  | EEV 电池故障
| AL029 EEPROM alarm EVD | 41 | 10042 | 1 | BOOL | Read |  | EEV EEPROM 报警
| AL030 Incomplete closing EVD | 42 | 10043 | 1 | BOOL | Read |  | EEV未完全关闭报警
| AL031 Emergency closing EVD | 43 | 10044 | 1 | BOOL | Read |  | EEV紧急关闭报警
| AL032 FW not compatible EVD | 44 | 10045 | 1 | BOOL | Read |  | EEV FW版本不匹配
| AL033 Config. error EVD | 45 | 10046 | 1 | BOOL | Read |  | EEV 配置错误
| AL034 EVD Driver offline | 46 | 10047 | 1 | BOOL | Read |  | EEV 离线报警
| AL035 BLDC-alarm:High startup DeltaP | 47 | 10048 | 1 | BOOL | Read |  | BLDC-启动压差过高
| AL036 BLDC-alarm:Compressor shut off | 48 | 10049 | 1 | BOOL | Read |  | BLDC-压缩机关闭
| AL037 BLDC-alarm:Out of Envelope | 49 | 10050 | 1 | BOOL | Read |  | BLDC-超出运行区间
| AL038 BLDC-alarm:Starting fail wait | 50 | 10051 | 1 | BOOL | Read |  | BLDC-压缩机启动失败
| AL039 BLDC-alarm:Starting fail exceeded | 51 | 10052 | 1 | BOOL | Read |  | BLDC-压缩机启动失败
| AL040 BLDC-alarm:Low delta pressure | 52 | 10053 | 1 | BOOL | Read |  | BLDC-低压差
| AL041 BLDC-alarm:High discarge gas temp | 53 | 10054 | 1 | BOOL | Read |  | BLDC-高排气温度
| AL042 Envelope-alarm:High compressor ratio | 54 | 10055 | 1 | BOOL | Read |  | Envelope-高压比
| AL043 Envelope-alarm:High discharge press. | 55 | 10056 | 1 | BOOL | Read |  | Envelope-高排气压力
| AL044 Envelope-alarm:High current | 56 | 10057 | 1 | BOOL | Read |  | Envelope-高电流
| AL045 Envelope-alarm:High suction pressure | 57 | 10058 | 1 | BOOL | Read |  | Envelope-高吸气压力
| AL046 Envelope-alarm:Low compressor ratio | 58 | 10059 | 1 | BOOL | Read |  | Envelope-低压比
| AL047 Envelope-alarm:Low pressure diff. | 59 | 10060 | 1 | BOOL | Read |  | Envelope-低压差
| AL048 Envelope-alarm:Low discharge pressure | 60 | 10061 | 1 | BOOL | Read |  | Envelope-低排气压力
| AL049 Envelope-alarm:Low suction pressure | 61 | 10062 | 1 | BOOL | Read |  | Envelope-低吸气压力
| AL050 Envelope-alarm:High discharge temp. | 62 | 10063 | 1 | BOOL | Read |  | Envelope-高排气温度
| AL051 Power+ alarm:01-Overcurrent | 63 | 10064 | 1 | BOOL | Read |  | Power+01-过电流
| AL052 Power+ alarm:02-Motor overload | 64 | 10065 | 1 | BOOL | Read |  | Power+02-电机过载
| AL053 Power+ alarm:03-DCbus overvoltage | 65 | 10066 | 1 | BOOL | Read |  | Power+03-DCbus过电压
| AL054 Power+ alarm:04-DCbus undervoltage | 66 | 10067 | 1 | BOOL | Read |  | Power+04-DCbus欠压
| AL055 Power+ alarm:05-Drive overtemp. | 67 | 10068 | 1 | BOOL | Read |  | Power+05-变频器过热
| AL056 Power+ alarm:06-Drive undertemp. | 68 | 10069 | 1 | BOOL | Read |  | Power+06-变频器欠温
| AL057 Power+ alarm:07-Overcurrent HW | 69 | 10070 | 1 | BOOL | Read |  | Power+07-过电流HW
| AL058 Power+ alarm:08-Motor overtemp. | 70 | 10071 | 1 | BOOL | Read |  | Power+08-电机过热
| AL059 Power+ alarm:09-IGBT module error | 71 | 10072 | 1 | BOOL | Read |  | Power+09-IGBT模块故障
| AL060 Power+ alarm:10-CPU error | 72 | 10073 | 1 | BOOL | Read |  | Power+10-CPU故障
| AL061 Power+ alarm:11-Parameter default | 73 | 10074 | 1 | BOOL | Read |  | Power+11-参数缺失
| AL062 Power+ alarm:12-DCbus ripple | 74 | 10075 | 1 | BOOL | Read |  | Power+12-母线电压波动
| AL063 Power+ alarm:13-Data comm. Fault | 75 | 10076 | 1 | BOOL | Read |  | Power+13-数据通讯故障
| AL064 Power+ alarm:14-Thermistor fault | 76 | 10077 | 1 | BOOL | Read |  | Power+14-热敏电阻故障
| AL065 Power+ alarm:15-Autotuning fault | 77 | 10078 | 1 | BOOL | Read |  | Power+15-自动调节故障
| AL066 Power+ alarm:16-Drive disabled | 78 | 10079 | 1 | BOOL | Read |  | Power+16-变频器禁用
| AL067 Power+ alarm:17-Motor phase fault | 79 | 10080 | 1 | BOOL | Read |  | Power+17-电机相序故障
| AL068 Power+ alarm:18-Internal fan fault | 80 | 10081 | 1 | BOOL | Read |  | Power+18-风机故障
| AL069 Power+ alarm:19-Speed fault | 81 | 10082 | 1 | BOOL | Read |  | Power+19-速度故障
| AL070 Power+ alarm:20-PFC module error | 82 | 10083 | 1 | BOOL | Read |  | Power+20-PFC模块故障
| AL071 Power+ alarm:21-PFC overvoltage | 83 | 10084 | 1 | BOOL | Read |  | Power+21-PFC过电压
| AL072 Power+ alarm:22-PFC undervoltage | 84 | 10085 | 1 | BOOL | Read |  | Power+22-PFC欠压
| AL073 Power+ alarm:23-STO DetectionError | 85 | 10086 | 1 | BOOL | Read |  | Power+23-STO错误检测
| AL074 Power+ alarm:24-STO DetectionError | 86 | 10087 | 1 | BOOL | Read |  | Power+24-STO错误检测
| AL075 Power+ alarm:25-Ground fault | 87 | 10088 | 1 | BOOL | Read |  | Power+25-地线故障
| AL076 Power+ alarm:26-Internal error 1 | 88 | 10089 | 1 | BOOL | Read |  | Power+26-CPU同步错误1
| AL077 Power+ alarm:27-Internal error 2 | 89 | 10090 | 1 | BOOL | Read |  | Power+27-CPU同步错误2
| AL078 Power+ alarm:28-Drive overload | 90 | 10091 | 1 | BOOL | Read |  | Power+28-变频器过载
| AL079 Power+ alarm:29-uC safety fault | 91 | 10092 | 1 | BOOL | Read |  | Power+29：uC safety fault
| AL080 Power+ alarm:98-Unexpected restart | 92 | 10093 | 1 | BOOL | Read |  | Power+98：Unexpected restart
| AL081 Power+ alarm:99-Unexpected stop | 93 | 10094 | 1 | BOOL | Read |  | Power+99：Unexpected stop
| AL082 Power+ safety alarm:01-Current meas.fault | 94 | 10095 | 1 | BOOL | Read |  | Power+ safety alarm:01-Current meas.fault
| AL083 Power+ safety alarm:02-Current unbalanced | 95 | 10096 | 1 | BOOL | Read |  | Power+ safety alarm:02-Current unbalanced
| AL084 Power+ safety alarm:03-Over current | 96 | 10097 | 1 | BOOL | Read |  | Power+ safety alarm:03-Over current
| AL085 Power+ safety alarm:04-STO alarm | 97 | 10098 | 1 | BOOL | Read |  | Power+ safety alarm:04-STO alarm
| AL086 Power+ safety alarm:05-STO hardware alarm | 98 | 10099 | 1 | BOOL | Read |  | Power+ safety alarm:05-STO hardware alarm
| AL087 Power+ safety alarm:06-PowerSupply missing | 99 | 10100 | 1 | BOOL | Read |  | Power+ safety alarm:06-PowerSupply missing
| AL088 Power+ safety alarm:07-HW fault cmd.buffer | 100 | 10101 | 1 | BOOL | Read |  | Power+ safety alarm:07-HW fault cmd.buffer
| AL089 Power+ safety alarm:08-HW fault heater c. | 101 | 10102 | 1 | BOOL | Read |  | Power+ safety alarm:08-HW fault heater c.
| AL090 Power+ safety alarm:09-Data comm. Fault | 102 | 10103 | 1 | BOOL | Read |  | Power+ safety alarm:09-Data comm. Fault
| AL091 Power+ safety alarm:10-Compr. stall detect | 103 | 10104 | 1 | BOOL | Read |  | Power+ safety alarm:10-Compr. stall detect
| AL092 Power+ safety alarm:11-DCbus over current | 104 | 10105 | 1 | BOOL | Read |  | Power+ safety alarm:11-DCbus over current
| AL093 Power+ safety alarm:12-HWF DCbus current | 105 | 10106 | 1 | BOOL | Read |  | Power+ safety alarm:12-HWF DCbus current
| AL094 Power+ safety alarm:13-DCbus voltage | 106 | 10107 | 1 | BOOL | Read |  | Power+ safety alarm:13-DCbus voltage
| AL095 Power+ safety alarm:14-HWF DCbus voltage | 107 | 10108 | 1 | BOOL | Read |  | Power+ safety alarm:14-HWF DCbus voltage
| AL096 Power+ safety alarm:15-Input voltage | 108 | 10109 | 1 | BOOL | Read |  | Power+ safety alarm:15-Input voltage
| AL097 Power+ safety alarm:16-HWF input voltage | 109 | 10110 | 1 | BOOL | Read |  | Power+ safety alarm:16-HWF input voltage
| AL098 Power+ safety alarm:17-DCbus power alarm | 110 | 10111 | 1 | BOOL | Read |  | Power+ safety alarm:17-DCbus power alarm
| AL099 Power+ safety alarm:18-HWF power mismatch | 111 | 10112 | 1 | BOOL | Read |  | Power+ safety alarm:18-HWF power mismatch
| AL100 Power+ safety alarm:19-NTC over temp. | 112 | 10113 | 1 | BOOL | Read |  | Power+ safety alarm:19-NTC over temp.
| AL100 Power+ safety alarm:20-NTC under temp. | 113 | 10114 | 1 | BOOL | Read |  | Power+ safety alarm:20-NTC under temp.
| AL102 Power+ safety alarm:21-NTC fault | 114 | 10115 | 1 | BOOL | Read |  | Power+ safety alarm:21-NTC fault
| AL103 Power+ safety alarm:22-HWF sync fault | 115 | 10116 | 1 | BOOL | Read |  | Power+ safety alarm:22-HWF sync fault
| AL104 Power+ safety alarm:23-Invalid parameter | 116 | 10117 | 1 | BOOL | Read |  | Power+ safety alarm:23-Invalid parameter
| AL105 Power+ safety alarm:24-FW fault | 117 | 10118 | 1 | BOOL | Read |  | Power+ safety alarm:24-FW fault
| AL106 Power+ safety alarm:25-HW fault | 118 | 10119 | 1 | BOOL | Read |  | Power+ safety alarm:25-HW fault
| AL107 Power+ safety alarm:26-reseved | 119 | 10120 | 1 | BOOL | Read |  | Power+ safety alarm:26-reseved
| AL108 Power+ safety alarm:27-reseved | 120 | 10121 | 1 | BOOL | Read |  | Power+ safety alarm:27-reseved
| AL109 Power+ safety alarm:28-reseved | 121 | 10122 | 1 | BOOL | Read |  | Power+ safety alarm:28-reseved
| AL110 Power+ safety alarm:29-reseved | 122 | 10123 | 1 | BOOL | Read |  | Power+ safety alarm:29-reseved
| AL111 Power+ safety alarm:30-reseved | 123 | 10124 | 1 | BOOL | Read |  | Power+ safety alarm:30-reseved
| AL112 Power+ safety alarm:31-reseved | 124 | 10125 | 1 | BOOL | Read |  | Power+ safety alarm:31-reseved
| AL113 Power+ safety alarm:32-reseved | 125 | 10126 | 1 | BOOL | Read |  | Power+ safety alarm:32-reseved
| AL114 Power+ alarm:Power+ offline | 126 | 10127 | 1 | BOOL | Read |  | 变频器离线报警
| AL115 EEV alarm:Low superheat | 127 | 10128 | 1 | BOOL | Read |  | EEV低过热度报警
| AL116 EEV alarm:LOP | 128 | 10129 | 1 | BOOL | Read |  | EEV LOP报警
| AL117 EEV alarm:MOP | 129 | 10130 | 1 | BOOL | Read |  | EEV MOP报警
| AL118 EEV alarm:High condens.temp. | 130 | 10131 | 1 | BOOL | Read |  | EEV高冷凝温度报警
| AL119 EEV alarm:Low suction temp. | 131 | 10132 | 1 | BOOL | Read |  | EEV低吸气温度报警
| AL120 EEV alarm:Motor error | 132 | 10133 | 1 | BOOL | Read |  | EEV电机故障
| AL121 EEV alarm:Self Tuning | 133 | 10134 | 1 | BOOL | Read |  | EEV自应PID错误
| AL122 EEV alarm:Emergency closing | 134 | 10135 | 1 | BOOL | Read |  | EEV 紧急关闭报警
| AL123 EEV alarm:Temperature delta | 135 | 10136 | 1 | BOOL | Read |  | EEV温差保护
| AL124 EEV alarm:Pressure delta | 136 | 10137 | 1 | BOOL | Read |  | EEV压差保护
| AL125 EEV alarm:Param.range error | 137 | 10138 | 1 | BOOL | Read |  | EEV范围错误
| AL126 EEV alarm:ServicePosit% err | 138 | 10139 | 1 | BOOL | Read |  | EEV位置信号错误
| AL127 EEV alarm:ValveID pin error | 139 | 10140 | 1 | BOOL | Read |  | EEV序号错误
| AL128 Low press alarm | 140 | 10141 | 1 | BOOL | Read |  | 低压报警
| AL129 High press alarm | 141 | 10142 | 1 | BOOL | Read |  | 高压报警
| AL130 Disc.temp.probe error | 142 | 10143 | 1 | BOOL | Read |  | 排气温度探头报警
| AL131 Suct.temp.probe error | 143 | 10144 | 1 | BOOL | Read |  | 吸气温度探头报警
| AL132 Disc.press.probe error | 144 | 10145 | 1 | BOOL | Read |  | 排气压力探头报警
| AL133 Suct.press.probe error | 145 | 10146 | 1 | BOOL | Read |  | 吸气压力探头报警
| AL134 Tank temp.probe error | 146 | 10147 | 1 | BOOL | Read |  | 水箱温度探头报警
| AL135 EVI SuctT.probe error | 147 | 10148 | 1 | BOOL | Read |  | EVI 吸气温度探头报警
| AL136 EVI SuctP.probe error | 148 | 10149 | 1 | BOOL | Read |  | EVI 吸气压力探头报警
| AL137 Flow switch alarm | 149 | 10150 | 1 | BOOL | Read |  | 水流开关报警
| AL138 High temp. alarm | 150 | 10151 | 1 | BOOL | Read |  | 高出水温度报警
| AL139 Low temp. alarm | 151 | 10152 | 1 | BOOL | Read |  | 低出水温度报警
| AL140 Temp.delta alarm | 152 | 10153 | 1 | BOOL | Read |  | 进出水温差报警
| AL141 EVI alarm:Param.range error | 153 | 10154 | 1 | BOOL | Read |  | EVI范围错误
| AL142 EVI alarm:Low superheat | 154 | 10155 | 1 | BOOL | Read |  | EVI 低过热度报警
| AL143 EVI alarm:LOP | 155 | 10156 | 1 | BOOL | Read |  | EVI LOP报警
| AL144 EVI alarm:MOP | 156 | 10157 | 1 | BOOL | Read |  | EVI MOP报警
| AL145 EVI alarm:High condens.temp. | 157 | 10158 | 1 | BOOL | Read |  | EVI高冷凝温度报警
| AL146 EVI alarm:Low suction temp. | 158 | 10159 | 1 | BOOL | Read |  | EVI低吸气温度报警
| AL147 EVI alarm:Motor error | 159 | 10160 | 1 | BOOL | Read |  | EVI电机故障
| AL148 EVI alarm:Self Tuning | 160 | 10161 | 1 | BOOL | Read |  | EVI自适应PID错误
| AL149 EVI alarm:Emergency closing | 161 | 10162 | 1 | BOOL | Read |  | EVI紧急关闭
| AL150 EVI alarm:ServicePosit% err | 162 | 10163 | 1 | BOOL | Read |  | EVI位置信号错误
| AL151 EVI alarm:ValveID pin error | 163 | 10164 | 1 | BOOL | Read |  | EVI序号错误
| AL152 Supply power error | 164 | 10165 | 1 | BOOL | Read |  | 电源频率波动报警
| AL153 Fan1 fault | 165 | 10166 | 1 | BOOL | Read |  | 调速风机1故障
| AL154 Fan2 fault | 166 | 10167 | 1 | BOOL | Read |  | 调速风机2故障
| AL155 Fans Offline | 167 | 10168 | 1 | BOOL | Read |  | 调速风机通信离线
| AL165 Slave1 Offline | 168 | 10169 | 1 | BOOL | Read |  | 1#从机离线
| AL166 Master Offline | 169 | 10170 | 1 | BOOL | Read |  | 主机离线
| AL167 Slave2 Offline | 170 | 10171 | 1 | BOOL | Read |  | 2#从机离线
| AL168 Slave3 Offline | 171 | 10172 | 1 | BOOL | Read |  | 3#从机离线
| AL169 Slave4 Offline | 172 | 10173 | 1 | BOOL | Read |  | 4#从机离线
| AL170 Slave5 Offline | 173 | 10174 | 1 | BOOL | Read |  | 5#从机离线
| AL171 Slave6 Offline | 174 | 10175 | 1 | BOOL | Read |  | 6#从机离线
| AL172 Slave7 Offline | 175 | 10176 | 1 | BOOL | Read |  | 7#从机离线
| AL173 Slave8 Offline | 176 | 10177 | 1 | BOOL | Read |  | 8#从机离线
| AL174 Slave9 Offline | 177 | 10178 | 1 | BOOL | Read |  | 9#从机离线